	                      DTNA Santiago        

                 New Topcoat Paint Facility                     

[image: image1.jpg]DAIMLER



[image: image2.png]PNEU - MECH PAINT FACILITIES







	

	


                                              Controls Specification

Design  and  Drawings
· Application analysis, formulation of control system design concept and selection of basic control components
· Calculation and sizing of control elements
· Control system electrical schematic drawings
· Panel layout drawings including Bill of Material for panel equipment and field mounted equipment.
· Conduit riser diagrams (one-line diagrams) and control system component location drawings for electrical installation.
· PLC rack drawings (slot assignments) with dip switch and jumper plug settings.
· PLC rack and system interconnect drawings.
· Development and Documentation of PLC application software (ladder logic) and PID algorithms.
· Preparation of instruction, operating and maintenance manuals
Field Supervisory Services
· Job site inspection (field check) for final design data and miscellaneous information required to complete the control system design.
· Instructions to, and discussion of, drawings with supervisors of installing trades
· Check out of electrical installation with installing electricians; any required standby electricians to be furnished by others 
· Calibration, commissioning and tuning of control systems
· Assistance on balancing and adjustment of the process equipment
· Assistance during performance tests of control systems and process equipment.
· Instructions to operating personnel during actual start-up, operation, and shut-down of the equipment.  
· Formal (classroom) training class for Operating and Maintenance personnel; one, eight (8) hour class for up to 25 people will be provided.
· Maintenance training classes for the maintenance personnel
· Warranty service for one (1) year on the completed system when failures occur due to defects in workmanship or material
BASE/COAT Robotic and Manual (Master control panel)
CONTROL PANELS, ONE ( 1 ) REQUIRED

(1)NEMA 12 free standing Master Control Panel (200A )including furnishing, mounting, and wiring the main disconnect, a control circuit transformer, branch circuit fusing as required, necessary control relays, time delay relays, programmable logic controller remote I/O with Panelview 600, push buttons and pilot lights; includes motor control for  the following motors:
	1 - Flash-off exhaust 3HP

	1 - Clean room air supply 7.5 HP

	1 - Sludge Pump #1 20 HP

	1 - Sludge Pump #2 20 HP

	1 - Sludge Pump #3 20 HP

	1 - Sludge Transfer Pump 5 HP
Motors with field mounted VFD’s


	1 - Air Supply #1 40 HP VFD

	1 - Air Supply #1 40 HP VFD

	1 - Tack-off exhaust 15 HP VFD

	1 - Tack-off exhaust 15 HP VFD

	1 - B.C. Spray booth exhaust 30HP VFD

	1 - B.C. Spray booth exhaust 30 HP VFD

	1 - B.C. Spray booth exhaust 40 HP VFD

	1 - B.C. Spray booth exhaust 40 HP VFD

	1 - C.C. Spray booth exhaust 30 HP VFD

	1 - C,C. Spray Booth exhaust 30 HP VFD

	1 - Air Supply #2 50 HP VFD

	1 - Air Supply #2 50 HP VFD


FRESH AIR SUPPLY CONTROLS, PER UNIT, one (1) REQUIRED

Dampers  and  Damper  Controls
2-Intake damper operators, two position, spring return to the closed position; 120/60 electric; Honeywell
2-Mounting bracket for support of damper operator above plus connecting linkage to operate damper; Honeywell
4-Damper limit switches to detect "damper open" position; for interlocking with the fan starter circuit; Allen Bradley
1-Damper operating relay, electric
Temperature Controls
1-Temperature Control; indicating, electric, modulating control with automatic reset and rate action (PID), 4-20 ma DC control signal output, input range field configurable; located in the PLC; A/B
1-Temperature Control Sensor, insertion type, 100 ohm platinum RTD; with 4- 20 ma transmitter; GIC
1-Temperature Control Motor, electric, modulating, non- spring return; for operation of the burner fuel valve (mounting bracket and linkage to be furnished with the device to be operated); 120/60 powered, 4-20 ma DC control signal input; Honeywell
1-High Temperature Limit; cuts off heat to protect equipment; auto resetting; 20 foot capillary type sensor; Honeywell UDC 2300.
1-Discharge Air Temperature Control; indicating, electric modulating control with automatic reset and rate action (PID), 4-20 ma DC control signal output, input range field configurable; located in the PLC; A/B
1-Discharge Air Control Sensor, duct mounting type, 100 ohm platinum RTD; with 4-20ma transmitter; GIC
1-Humidifier Coil Freeze Protection Low Temperature Limit; 20 foot averaging capillary type to be attached to leaving side of coils; auto-resetting; Honeywell L480B

1-Discharge Air Humidity Control; indicating, electric modulating control with automatic reset and rate action (PID); 4-20 ma DC output, input range field configurable;  located in the PLC; A/B.
1-Humidity Sensor/Transmitter matched to above controller; insertion type unit of "Bulk-Polymer" design to reduce maintenance; 4-20 ma DC output over 0-100% RH; Vaisala
1-Outside air high temperature limit switch to shut off burner when outside air temperature reaches desired discharge temperature; remote bulb capillary type, 0-100 deg F., 20 foot element; Honeywell T675A.1-
Low fire start relay; enables temperature control circuit after unit is started; electric.
Burner Safety Controls
2-Flame relay with wiring base; includes flame sensing amplifier with  dynamic self-check; timed trial for pilot flame is manual resetting; Honeywell RM 7838B
3-Flame detector matched to above flame relay; Ultra-violet type; one for pilot and main flame of single stage burner system; Honeywell C7061E.
2-Flame signal meter; indicates quality of flame signal; with special plug and leads to match flame relay above; Honeywell
1-Purge timer circuit; inhibits light off of burners until fans have run a sufficient time to allow four air changes; Eagle
1-Supply Fan Airflow (or Burner Differential Pressure) Switch to provide mechanical proving of fan operation and sufficient airflow for burner operation; Dwyer 1823-0
Miscellaneous  Controls
1-Filter differential pressure transmitter to signal PLC; including indicating gauge,  0-2" range; Dwyer 
1-Wet Pan Flush Solenoid valve, ¾” Stainless steel; Asco
1-Humidifier tank level control, float type; SJ Electrode
1-Humidifier Make-up valve; 1”, 120 vac, stainless steel; Asco
1-Humidifier water flow meter; ABB Kent
4-Humidifier water supply valves; 1”, 120 vac, stainless steel; Asco
1-Velocity Pressure sensor with 4-20 ma signal;
RECIRCULATING AIR SUPPLY CONTROLS, PER UNIT, ONE ( 1 ) REQUIRED

Dampers  and  Damper  Controls
1-Intake damper operators, two position, linear gear driven, 1200 in/lb torque; 120/60 electric; Jordan
1-Mounting bracket for support of damper operator above plus connecting linkage to operate damper.
2-Damper limit switches to detect "damper open" position; for interlocking with the fan starter circuit; Allen Bradley
1-Damper operating relay, electric

1-Recirculating damper operators, two position, linear gear driven, 1200 in/lb torque; 120/60 electric; Jordan
1-Mounting bracket for support of damper operator above plus connecting linkage to operate damper.
2-Damper limit switches to detect "damper open" position; for interlocking with the fan starter circuit; Allen Bradley
1-Damper operating relay, electric

 Temperature Controls
1-Temperature Control; indicating, electric, modulating control with automatic reset and rate action (PID), 4-20 ma DC control signal output, input range field configurable; located in the PLC; A/B
1-Temperature Control Sensor, insertion type, 100 ohm platinum RTD; with 4- 20 ma transmitter; GIC
1-Discharge Air Temperature Control; indicating, electric modulating control with automatic reset and rate action (PID), 4-20 ma DC control signal output, input range field configurable; located in the PLC; A/B
1-Discharge Air Control Sensor, duct mounting type, 100 ohm platinum RTD; with 4-20ma transmitter; GIC
1-Low Temperature Limit Switch, for discharge air or to protect cooling coils; requires timer to inhibit action during purge and warm-up period; auto resetting; Honeywell L480B
1-High temperature limit; reduces heat to minimum when air temperature exceeds filter media rating; auto reset; with insertion type sensor; Honeywell UDC2300

Miscellaneous  Controls
1-
Filter differential pressure transmitter to signal PLC; including indicating gauge,  0-2" range; Dwyer 
1-
Wet Pan Flush Solenoid valve, ¾” Stainless steel; Asco
1-
Supply Fan Airflow Switch to provide mechanical proving of fan operation and sufficient airflow for burner operation; Dwyer 1823-0
1-
Velocity Pressure sensor with 4-20 ma signal;
1-
LEL sensor with 4-20 ma input to the PLC; with sampling tupe for exhaust air; Gastech
· Lighting transformers, lighting circuit panels and fixtures. 
· Motor safety lockout switches (non-fused disconnect) required at motors *including auxiliary signal contacts if required. 
BOOTH SLUDGE SYSTEM

Controlled from Master Control Panel
2- Sludge Recirculation Pumps, 20 HP 
1- Sludge Transfer Pump; 5 HP
1- Pit Sump Pump, 5 HP 
Miscellaneous  Controls
2-Pump proven pressure transmitters, with 4- 20 ma output signal, loop powered; Ashcroft
1-Make-up ball valve, 2”, stainless steel body, 120 vac, on - off ; Apollo
1-Totalizing flow meter, with 4- 20 ma output signal; stainless steel body, 120 vac, 
2-Liquid level  system; for interlocking with the pump  starter circuit; with 4- 20 ma output, low level cutout switch and gauge; E & H
1-Totalizing meter with 4-20 ma output, 3”; ABB Kent
1-Flow Control Butterfly valve, 4”, 150 lb. Flanged connections, two position with limit switches to detect “valve open” and “valve closed” position, pneumatic, on - off, 60 psi plant air required, solenoid activated, 120 vac; 
1-Palin Filter Pressure transmitters, with 4-20 ma output; Ashcroft

PAINT CURE OVENS

CONTROL PANELS, ONE ( 1 ) REQUIRED

(1)NEMA 12 free standing Cure Oven Zone control panel (400A) including furnishing, mounting, and wiring the main disconnect, a control circuit transformer, branch circuit fusing as required, necessary control relays, time delay relays, programmable logic controller remote I/O with Panelview 600, push buttons and pilot lights; includes motor control for  the following motors:
Heater #1
2- Recirculation Fans, 20 HP
2- Air Seal Fan, 10 HP
1- Combustion Blower.1.5 HP
Heater #2
2- Recirculation Fans, 20 HP
2- Air Seal Fan, 10 HP
1- Combustion Blower1.5 HP
1- Oven Exhaust Fan 5 HP
OVEN ZONE CONTROLS, PER UNIT, TWO ( 2) REQUIRED

 Temperature Controls
1-Temperature Control; indicating, electric, modulating control with automatic reset and rate action (PID), 4-20 ma DC control signal output, input range field configurable; located in the PLC; A/B
1-Temperature Control Sensor, insertion type, 100 ohm platinum RTD; with 4- 20 ma transmitter; GIC
1-High Temperature Control Sensor, insertion type, 100 ohm platinum RTD;  GIC
1-Temperature Control Motor, electric, modulating, non- spring return; for operation of the burner fuel valve (mounting bracket and linkage to be furnished with the device to be operated); 120/60 powered, 4-20 ma DC control signal input; Honeywell
1-Temperature Limit; cuts off heat to protect equipment; auto resetting; 20 foot capillary type sensor; Honeywell UDC 2300.
1-Low fire start relay; enables temperature control circuit after unit is started; electric.

Burner Safety Controls
1-Flame relay with wiring base; includes flame sensing amplifier with  dynamic self-check; timed trial for pilot flame is manual resetting; Honeywell RM 7838B
2-Flame detector matched to above flame relay; Ultra-violet type; one for pilot and main flame of single stage burner system; Honeywell C7012E.
1-Flame signal meter; indicates quality of flame signal; with special plug and leads to match flame relay above; Honeywell
1-Purge timer circuit; inhibits light off of burners until fans have run a sufficient time to allow four air changes; Eagle
1-Supply Fan Airflow (or Burner Differential Pressure) Switch to provide mechanical proving of fan operation and sufficient airflow for burner operation; Dwyer 1823-0
 Miscellaneous  Controls
1-Filter differential pressure indication system including indicating gauge, three-way vent valves and airflow tips; 0-2" range; Dwyer Magnahelic 2002.  
1-Exhaust/RTO damper operators, two position, linear gear driven, 1200 in/lb torque; 120/60 electric; Jordan
1-Mounting bracket for support of damper operator above plus connecting linkage to operate damper.
2-Damper limit switches to detect "damper open" position; for interlocking with the fan starter circuit; Allen Bradley
1-Damper operating relay, electric

Controls Specification

Proprietary and Confidential


3/12/2012

