	                      DTNA Santiago        

                 New Topcoat Paint Facility                     

[image: image1.jpg]DAIMLER



[image: image2.png]PNEU - MECH PAINT FACILITIES







	

	

	



                                    Top Coat Prep Booth Specification

Top Coat  Prep Booth General Description

The Top Coat Prep Booth will be utilized for minor sand and prep prior to the Top Coat system.

  The Top Coat Prep Booth is a downdraft airflow design. The air supply plenum is located at the top of the booth with ducts. The exhaust air plenums are equipped with filters and are located on both sides of the booth at the floor level. 

   The Prep Booth system will draw air from the building and exhaust to building. 

Sanding Booth Operation

	ITEM
	DESCRIPTION

	Supply Air Conditions: 
	
	· Ambient

	Ventilation:
	
	· 100% Fresh Air

	Sanding Booth 
	Design:
	· 0,2 m/s downdraft

	Filtration:
	Exhaust Air:
	· Filter – 95% Efficient

	Lighting:
	Booths 
	· 1000 lux


Sanding Booth Process Zones / Dimensions

	ITEM
	DESCRIPTION

	Sanding Booth: 
	
	· 8000mm L x 6000mm W x 3700mm H - I.D.


 Sanding Booth Construction:

	ITEM
	DESCRIPTION

	Construction 
	Prep Booth Ceiling:
	· Bolted Construction

	Details:
	Strong Backs and        C-Channels
	· Mild Steel W Beam -3mm Aluminized Steel            C-Channel

	
	Mono Panels:
	· 1,5mm Aluminized Steel (Perforation 20%)

	Construction 
	Prep Booth Side and End Walls:
	· Bolted Construction

	Details:
	Strong Backs and        C-Channels
	· Mild Steel W Beam -3mm Aluminized Steel            C-Channel

	
	Mono Panels:

Door/Window Frames:

Window Gaskets:

Doors:

Wire Reinforced Windows:
	· 1,25mm Aluminized Steel

· 1,25mm Aluminized Steel

· Material to withstand MEK and MAK

· Size: 2000mm x 750mm, 110 degree swing - glass 450mm x 750mm
· 1200mm x 1200mm

	Construction:
	Exhaust Air Ductwork:
	· Flanged, Bolted and Caulked (6000mm Sections-Max)

	Details:
	Maximum Velocity:
	· Duct Sized for 10 m/s @ 100mm wc. Neg. Static Pressure

	
	Clean-Out Doors:
	· 600mm x 600mm Maximum 6000mm spacing

	
	Flanges and Stiffeners:
	· Mild Steel

	
	Duct Material:
	· 1,5mm Aluminized Steel

	Construction:
	Supply Air Ductwork:
	· Flanged, Bolted and Caulked (6000mmSections-Max)

	Details:
	Maximum Velocity:
	· Duct Sized for 10 m/s @ 100mm wc. Neg. Static Pressure

	
	Clean-Out Doors:
	· 600mm x 600mm Maximum 6000mm spacing 

	
	Flanges and Stiffeners:
	· Mild Steel

	
	Duct Material:
	· 1,5mm Aluminized Steel

	Floor:
	
	· Sized for 200 kg/m2 Live Load

	
	
	· Mild Steel Grating, 30mm x 5mm, 30mm c/c, Cross Bars on 100mm c/c

	
	
	· 30mm x 5mm Band on Both Ends of Bearing Bars

	
	
	· Maximum Weight of Grating Section – 30kg.

	
	
	· Support Structure, Mild Steel


Painting:

	ITEM
	DESCRIPTION

	Mild Steel:
	
	All Structural Steel Delivered to Site Shall be Shop Primed

	
	
	After Installation, (1) One Finish Coat

	Galvanized / Aluminized Steel:
	
	No Coating


Topcoat Prep Booth Specifications

Proprietary and Confidential


3/7/2012

